## Reg
RAPPORT DÉTAILLÉ
Statistiques de la régression
Coefficient de détermination multiple | 0.9917
Coefficient de détermination R^2 | 0.98346
Coefficient de détermination R^2 | 0.97106
Erreur-type | 0.085631
Observations | 8
ANALYSE DE VARIANCE
| Degré de liberté | Somme des carrés | Moyenne des carrés | F | Valeur critique de F
Régression | 3 | 1.744 | 0.58134 | 79.2807 | 0.00051009
Résidus | 4 | 0.029331 | 0.0073327
Total | 7 | 1.7733
| Coefficients | Erreur-type | Statistique t | Probabilité | Limite inférieure pour seuil de confiance = 95% | Limite supérieure pour seuil de confiance = 95% | Limite inférieure pour seuil de confiance = 95.0% | Limite supérieure pour seuil de confiance = 95.0%
Constante | 4.1799 | 0.4442 | 9.4098 | 0.00071092 | 2.9466 | 5.4132 | 2.9466 | 5.4132
log L | 1.4086 | 0.28195 | 4.9957 | 0.007513 | 0.62574 | 2.1914 | 0.62574 | 2.1914
log W | 1.0487 | 0.43831 | 2.3926 | 0.074956 | -0.16824 | 2.2656 | -0.16824 | 2.2656
log H | 0.50612 | 0.30349 | 1.6677 | 0.1707 | -0.33649 | 1.3487 | -0.33649 | 1.3487

## Bilan
| Power [W] | hS [W/K] | L [m] | W [m] | H [m] | Masse [kg] | Air DP [Pa] | Flow Air [m^3/min] | Air DP/Q^2 [Pa/(m^3/s)²] | Water DP [bar] | Flow Water [lpm] | Water DP/Q^2 [Pa/(m^3/s)²] | Liquid volume [l] | L/W | L/H | V
| 360 | 13.1 | 0.188 | 0.033 | 0.168 | 1.18 | 50 | 4 | 11250 | 0.1 | 7.6 | 623268698060.9418 | 0.05 | 5.697 | 1.119 | 0.0010423 | 1.5831 | 1.9734e+13
| 430 | 24.42 | 0.188 | 0.048 | 0.147 | 1.15 | 300 | 6 | 30000 | 0.75 | 11.4 | 2.0776e+12 | 0.131 | 3.9167 | 1.2789 | 0.0013265 | 4.7402 | 7.5176e+13
| 700 | 48.77 | 0.31 | 0.046 | 0.147 | 2.31 | 50 | 4 | 11250 | 0.4 | 7.6 | 2.4931e+12 | 0.205 | 6.7391 | 2.1088 | 0.0020962 | 4.4986 | 5.4709e+13
| 1230 | 69.917 | 0.301 | 0.064 | 0.229 | 2.99 | 250 | 14 | 4591.8367 | 0.6 | 7.6 | 3.7396e+12 | 0.288 | 4.7031 | 1.3144 | 0.0044115 | 4.1782 | 5.4253e+13
| 2000 | 132.465 | 0.505 | 0.064 | 0.229 | 4.99 | 50 | 11.2 | 1434.949 | 1 | 7.6 | 6.2327e+12 | 0.5 | 7.8906 | 2.2052 | 0.0074013 | 4.3236 | 5.3895e+13
| 2110 | 99.46 | 0.328 | 0.053 | 0.305 | 7.03 | 100 | 14.15 | 1797.9997 | 0.6 | 15.1 | 947326871628.4376 | 0.488 | 6.1887 | 1.0754 | 0.0053021 | 4.878 | 9.4695e+12
| 3000 | 195.76 | 0.588 | 0.053 | 0.305 | 8.21 | 25 | 14 | 459.1837 | 0.9 | 15.1 | 1.421e+12 | 0.844 | 11.0943 | 1.9279 | 0.009505 | 4.7061 | 7.9234e+12
| 7600 | 500 | 0.699 | 0.089 | 0.564 | 16.42 | 18.75 | 14.15 | 337.1249 | 0.2 | 37.8 | 50390526581.0028 | 1.737 | 7.8539 | 1.2394 | 0.035087 | 4.406 | 127818176374.0571
hS est | hS [W/K] |  | Air DP/Q^2 [Pa/(m^3/s)²] |  | Water DP/Q^2 [Pa/(m^3/s)²] | L [m] | W [m] | H [m] |  | log hS | log Air DP/Q² | log Water DP/Q² |  | log L | log W | log H
16.2834 | 13.1 | 11133.3343 | 11250 | 932207744451.7832 | 623268698060.9418 | 0.188 | 0.033 | 0.168 |  | 1.1173 | 4.0512 | 11.7947 |  | -0.72584 | -1.4815 | -0.77469
22.5448 | 24.42 | 27155.7127 | 30000 | 3.0934e+12 | 2.0776e+12 | 0.188 | 0.048 | 0.147 |  | 1.3877 | 4.4771 | 12.3176 |  | -0.72584 | -1.3188 | -0.83268
43.6124 | 48.77 | 7866.4343 | 11250 | 6.4285e+12 | 2.4931e+12 | 0.31 | 0.046 | 0.147 |  | 1.6882 | 4.0512 | 12.3967 |  | -0.50864 | -1.3372 | -0.83268
74.0339 | 69.917 | 6073.4817 | 4591.8367 | 1.4715e+12 | 3.7396e+12 | 0.301 | 0.064 | 0.229 |  | 1.8446 | 3.662 | 12.5728 |  | -0.52143 | -1.1938 | -0.64016
153.452 | 132.465 | 1814.28 | 1434.949 | 3.3687e+12 | 6.2327e+12 | 0.505 | 0.064 | 0.229 |  | 2.1221 | 3.1568 | 12.7947 |  | -0.29671 | -1.1938 | -0.64016
79.2653 | 99.46 | 2052.7436 | 1797.9997 | 349395637563.725 | 947326871628.4376 | 0.328 | 0.053 | 0.305 |  | 1.9976 | 3.2548 | 11.9765 |  | -0.48413 | -1.2757 | -0.5157
180.3691 | 195.76 | 525.2949 | 459.1837 | 889380676044.0801 | 1.421e+12 | 0.588 | 0.053 | 0.305 |  | 2.2917 | 2.662 | 12.1526 |  | -0.23062 | -1.2757 | -0.5157
540.9353 | 500 | 246.4177 | 337.1249 | 178741037257.9341 | 50390526581.0028 | 0.699 | 0.089 | 0.564 |  | 2.699 | 2.5278 | 10.7023 |  | -0.15552 | -1.0506 | -0.24872
Coef hS | 4.1799 | 1.4086 | 1.0487 | 0.50612
Coef AirDP | 3.2919 | -2.335 | 1.6724 | -1.9846
Coef WaterDP | 12.1046 | 1.6006 | 1.6229 | -4.4288

## 360
https://www.boydcorpdirect.com/6105g1-copper-tube-fin-heat-exchanger/6105g1/
| Débit eau | 1.8 | lpm | Dimensions
| Cp eau | 4185 | J/kg/K | L | 188 | mm
| Cp air | 1004 | J/kg/K | W | 33 | mm
| Rho air | 1.2 | kg/m^3 | H | 168 | mm
|  |  |  | Masse | 1.18 | kg
Ref | Power [W] | hS [W/K] | L [m] | W [m] | H [m] | Masse [kg] | Air DP [Pa] | Flow Air [m^3/min] | Water DP [bar] | Flow Water [lpm]
6105g1 | 360 | 13.102 | 0.188 | 0.033 | 0.168 | 1.18 | 50 | 4 | 0.1 | 7.6
Efficacité | AirFlow | Q/dT | Cmin | Cmax | Efficacite | Vitesse air | Cr=Cmin/Cmax | NUT=AsU/Cmin | Efficacité calculée | Erreur | Erreur ^2
| m^3/min | W/°C | W/K | W/K | - | m/s
| 0 | 0 | 0 | 125.55 | 1 | 0 | 0 |  | 1
| 0.5 | 6 | 10.04 | 125.55 | 0.59761 | 0.26385 | 0.079968 | 1.305 | 0.71143 | 0.11382 | 0.012955
| 1 | 9.5 | 20.08 | 125.55 | 0.47311 | 0.52769 | 0.15994 | 0.65249 | 0.46016 | -0.012949 | 0.00016768
| 1.5 | 11.5 | 30.12 | 125.55 | 0.38181 | 0.79154 | 0.2399 | 0.43499 | 0.33558 | -0.046228 | 0.002137
| 2 | 12.8 | 40.16 | 125.55 | 0.31873 | 1.0554 | 0.31987 | 0.32624 | 0.26317 | -0.055552 | 0.003086
| 2.5 | 14 | 50.2 | 125.55 | 0.27888 | 1.3192 | 0.39984 | 0.261 | 0.21614 | -0.062747 | 0.0039372
[10 empty] | Somme erreur | 0.022283
Dimensions L x W x H
7.4" x 1.3" x 6.6" (188 mm x 33 mm x 168 mm)
Performance
360 W (1,230 BTU/Hr)
Fluid Compatibility
Water, Common Coolants
Wetted Path
Copper
Type
Tube-Fin Liquid-to-Air
Fluid Volume
3 in³ (50 ml)
Fin Material
Copper
Maximum Temperature
200°C (400°F)
Maximum Pressure
150 psi (10 BAR)
Maximum Flow Rate
2.0 gpm (7.6 lpm)
Liquid Pressure Drop
2.0 psi (0.1 BAR)
Air Pressure Drop
0.20 in H₂O (49.82 Pa)
Fan Plate
Included
Finish
Painted Black
Shipping Weight
2.6 lb (1.18 kg)

## 430
https://www.boydcorpdirect.com/6110g1-copper-tube-fin-heat-exchanger/6110g1/
| Débit eau | 1.8 | lpm | Dimensions
| Cp eau | 4185 | J/kg/K | L | 188 | mm
| Cp air | 1004 | J/kg/K | W | 48 | mm
| Rho air | 1.2 | kg/m^3 | H | 147 | mm
|  |  |  | Masse | 1.15 | kg
Ref | Power [W] | AsU | L [m] | W [m] | H [m] | Masse [kg] | Air DP [Pa] | Flow Air [m^3/min] | Water DP [bar] | Flow Water [lpm]
6110G1 | 430 | 24.4199 | 0.188 | 0.048 | 0.147 | 1.15 | 300 | 6 | 0.75 | 11.4
Efficacité | AirFlow | Q/dT | Cmin | Cmax | Efficacite | Vitesse air | Cr=Cmin/Cmax | NUT=AsU/Cmin | Efficacité calculée | Erreur | Erreur ^2
| m^3/min | W/°C | W/K | W/K | - | m/s
| 0 | 0 | 0 | 125.55 | 1 | 0 | 0 |  | 1
| 0.5 | 8 | 10.04 | 125.55 | 0.79681 | 0.30154 | 0.079968 | 2.4323 | 0.89436 | 0.097545 | 0.0095151
| 1 | 13 | 20.08 | 125.55 | 0.64741 | 0.60308 | 0.15994 | 1.2161 | 0.6703 | 0.022886 | 0.00052379
| 1.5 | 16 | 30.12 | 125.55 | 0.53121 | 0.90462 | 0.2399 | 0.81075 | 0.51978 | -0.011427 | 0.00013058
| 2 | 18.5 | 40.16 | 125.55 | 0.46066 | 1.2062 | 0.31987 | 0.60806 | 0.42109 | -0.039564 | 0.0015653
| 2.5 | 20.5 | 50.2 | 125.55 | 0.40837 | 1.5077 | 0.39984 | 0.48645 | 0.35273 | -0.055632 | 0.0030949
[10 empty] | Somme erreur | 0.01483
Dimensions L x W x H
7.4" x 1.8" x 5.8" (188 mm x 46 mm x 147 mm)
Performance
430 W (1468 BTU/Hr)
Fluid Compatibility
Water, Common Coolants
Wetted Path
Copper
Type
Tube-Fin Liquid-to-Air
Fluid Volume
8 in³ (131 ml)
Fin Material
Copper
Maximum Temperature
200°C (400°F)
Maximum Pressure
150 psi (10 BAR)
Maximum Flow Rate
2.0 gpm (7.6 lpm)
Liquid Pressure Drop
5.0 psi (0.4 BAR)
Air Pressure Drop
0.30 in H₂O (74.73 Pa)
Fan Plate
Included
Finish
Painted Black
Shipping Weight
2.6 lb (1.18 kg)

## 700
https://www.boydcorpdirect.com/6120g1-copper-tube-fin-heat-exchanger/6120g1/
| Débit eau | 3.7 | lpm | Dimensions
| Cp eau | 4185 | J/kg/K | L | 310 | mm
| Cp air | 1004 | J/kg/K | W | 46 | mm
| Rho air | 1.2 | kg/m^3 | H | 147 | mm
|  |  |  | Masse | 2.31 | kg
Ref | Power [W] | AsU | L [m] | W [m] | H [m] | Masse [kg] | Air DP [Pa] | Flow Air [m^3/min] | Water DP [bar] | Flow Water [lpm]
6120g1 | 700 | 48.7731 | 0.31 | 0.046 | 0.147 | 2.31 | 50 | 4 | 0.4 | 7.6
Efficacité | AirFlow | Q/dT | Cmin | Cmax | Efficacite | Vitesse air | Cr=Cmin/Cmax | NUT=AsU/Cmin | Efficacité calculée | Erreur | Erreur ^2
| m^3/min | W/°C | W/K | W/K | - | m/s
| 0 | 0 | 0 | 258.075 | 1 | 0 | 0 |  | 1
| 1 | 16 | 20.08 | 258.075 | 0.79681 | 0.36574 | 0.077807 | 2.4289 | 0.89455 | 0.09774 | 0.0095531
| 1.5 | 23 | 30.12 | 258.075 | 0.76361 | 0.54861 | 0.11671 | 1.6193 | 0.77444 | 0.010824 | 0.00011715
| 2 | 27 | 40.16 | 258.075 | 0.67231 | 0.73148 | 0.15561 | 1.2145 | 0.67072 | -0.0015869 | 2.5182e-06
| 2.5 | 31 | 50.2 | 258.075 | 0.61753 | 0.91434 | 0.19452 | 0.97158 | 0.58719 | -0.030338 | 0.0009204
| 3 | 34 | 60.24 | 258.075 | 0.56441 | 1.0972 | 0.23342 | 0.80965 | 0.52027 | -0.044136 | 0.001948
[10 empty] | Somme erreur | 0.012541
Dimensions L x W x H
12.2" x 1.8" x 5.8" (310 mm x 46 mm x 147 mm)
Performance
700 W (2389 BTU/Hr)
Fluid Compatibility
Water, Common Coolants
Wetted Path
Copper
Type
Tube-Fin Liquid-to-Air
Fluid Volume
12.5 in³ (205 ml)
Fin Material
Copper
Maximum Temperature
200°C (400°F)
Maximum Pressure
150 psi (10 BAR)
Maximum Flow Rate
2.0 gpm (7.6 lpm)
Liquid Pressure Drop
5.5 psi (0.4 BAR)
Air Pressure Drop
0.15 in H₂O (37.37 Pa)
Fan Plate
Included
Finish
Painted Black
Shipping Weight
5.1 lb (2.31 kg)

## 1230
https://www.boydcorpdirect.com/6220g1-copper-tube-fin-heat-exchanger/6220g1/
| Débit eau | 3.7 | lpm | Dimensions
| Cp eau | 4185 | J/kg/K | L | 301 | mm
| Cp air | 1004 | J/kg/K | W | 64 | mm
| Rho air | 1.2 | kg/m^3 | H | 229 | mm
|  |  |  | Masse | 2.99 | kg
Ref | Power [W] | AsU | L [m] | W [m] | H [m] | Masse [kg] | Air DP [Pa] | Flow Air [m^3/min] | Water DP [bar] | Flow Water [lpm]
6110G1 | 1230 | 63.917 | 0.301 | 0.064 | 0.229 | 2.99 | 250 | 14 | 0.6 | 7.6
Efficacité | AirFlow | Q/dT | Cmin | Cmax | Efficacite | Vitesse air | Cr=Cmin/Cmax | NUT=AsU/Cmin | Efficacité calculée | Erreur | Erreur ^2
| m^3/min | W/°C | W/K | W/K | - | m/s
| 0 | 0 | 0 | 258.075 | 1 | 0 | 0 |  | 1
| 1 | 15 | 20.08 | 258.075 | 0.74701 | 0.24179 | 0.077807 | 3.1831 | 0.94477 | 0.19776 | 0.039108
| 2 | 29 | 40.16 | 258.075 | 0.72211 | 0.48359 | 0.15561 | 1.5916 | 0.75977 | 0.037663 | 0.0014185
| 3 | 38 | 60.24 | 258.075 | 0.63081 | 0.72538 | 0.23342 | 1.061 | 0.60988 | -0.02093 | 0.00043808
| 4 | 44 | 80.32 | 258.075 | 0.54781 | 0.96718 | 0.31123 | 0.79578 | 0.50371 | -0.044099 | 0.0019447
| 5 | 50 | 100.4 | 258.075 | 0.49801 | 1.209 | 0.38903 | 0.63662 | 0.42706 | -0.070946 | 0.0050333
[10 empty] | Somme erreur | 0.047942
Dimensions L x W x H
11.9" x 2.5" x 9.0" (301 mm x 64 mm x 229 mm)
Performance
1240 W (4232 BTU/Hr
Fluid Compatibility
Water, Common Coolants
Wetted Path
Copper
Type
Tube-Fin Liquid-to-Air
Fluid Volume
17.5 in³ (288 ml)
Fin Material
Copper
Maximum Temperature
200°C (400°F)
Maximum Pressure
150 psi (10 BAR)
Maximum Flow Rate
2.0 gpm (7.6 lpm)
Liquid Pressure Drop
7.9 psi (0.6 BAR)
Air Pressure Drop
0.20 in H₂O (49.82 Pa)
Fan Plate
Included
Finish
Painted Black
Shipping Weight
6.6 lb (2.99 kg)

## 2000
https://www.boydcorpdirect.com/6220g1-copper-tube-fin-heat-exchanger/6220g1/
| Débit eau | 3.7 | lpm | Dimensions
| Cp eau | 4185 | J/kg/K | L | 505 | mm
| Cp air | 1004 | J/kg/K | W | 64 | mm
| Rho air | 1.2 | kg/m^3 | H | 229 | mm
|  |  |  | Masse | 4.99 | kg
| Power [W] | AsU | L [m] | W [m] | H [m] | Masse [kg] | Air DP [Pa] | Flow Air [m^3/min] | Water DP [bar] | Flow Water [lpm]
| 2000 | 132.4653 | 0.505 | 0.064 | 0.229 | 4.99 | 50 | 11.2 | 1 | 7.6
Efficacité | AirFlow | Q/dT | Cmin | Cmax | Efficacite | Vitesse air | Cr=Cmin/Cmax | NUT=AsU/Cmin | Efficacité calculée | Erreur | Erreur ^2
| m^3/min | W/°C | W/K | W/K | - | m/s
| 0 | 0 | 0 | 258.075 | 1 | 0 | 0 |  | 1
| 2 | 35 | 40.16 | 258.075 | 0.87151 | 0.28824 | 0.15561 | 3.2984 | 0.93447 | 0.062956 | 0.0039634
| 4 | 55 | 80.32 | 258.075 | 0.68476 | 0.57648 | 0.31123 | 1.6492 | 0.73342 | 0.048658 | 0.0023676
| 6 | 70 | 120.48 | 258.075 | 0.58101 | 0.86472 | 0.46684 | 1.0995 | 0.57859 | -0.002415 | 5.832e-06
| 8 | 82 | 160.64 | 258.075 | 0.51046 | 1.153 | 0.62245 | 0.82461 | 0.4719 | -0.03856 | 0.0014869
| 10 | 90 | 200.8 | 258.075 | 0.44821 | 1.4412 | 0.77807 | 0.65969 | 0.39623 | -0.051981 | 0.002702
[10 empty] | Somme erreur | 0.010526
Dimensions L x W x H
19.9" x 2.5" x 9.0" (505 mm x 64 mm x 229 mm)
Performance
2000 W (6826 BTU/Hr)
Fluid Compatibility
Water, Common Coolants
Wetted Path
Copper
Type
Tube-Fin Liquid-to-Air
Fluid Volume
30.5 in³ (500 ml)
Fin Material
Copper
Maximum Temperature
200°C (400°F)
Maximum Pressure
150 psi (10 BAR)
Maximum Flow Rate
2.0 gpm (7.6 lpm)
Liquid Pressure Drop
14.0 psi (1.0 BAR)
Air Pressure Drop
0.18 in H₂O (44.84 Pa)
Fan Plate
Included
Finish
Painted Black
Shipping Weight
11 lb (4.99 kg)

## 2110
https://www.boydcorpdirect.com/6310g3-copper-tube-fin-heat-exchanger/6310g3/
| Débit eau | 3.7 | lpm | Dimensions
| Cp eau | 4185 | J/kg/K | L | 328 | mm
| Cp air | 1004 | J/kg/K | W | 53 | mm
| Rho air | 1.2 | kg/m^3 | H | 305 | mm
|  |  |  | Masse | 7.03 | kg
| Power [W] | AsU | L [m] | W [m] | H [m] | Masse [kg] | Air DP [Pa] | Flow Air [m^3/min] | Water DP [bar] | Flow Water [lpm]
| 2110 | 99.4602 | 0.328 | 0.053 | 0.305 | 7.03 | 100 | 14.15 | 0.6 | 15.1
Efficacité | AirFlow | Q/dT | Cmin | Cmax | Efficacite | Vitesse air | Cr=Cmin/Cmax | NTU=AsU/Cmin | Efficacité calculée | Erreur | Erreur ^2
| m^3/min | W/°C | W/K | W/K | - | m/s
| 0 | 0 | 0 | 258.075 | 1 | 0 | 0 |  | 1
| 1 | 18 | 20.08 | 258.075 | 0.89641 | 0.1666 | 0.077807 | 4.9532 | 0.98695 | 0.090532 | 0.0081961
| 2 | 33 | 40.16 | 258.075 | 0.82171 | 0.3332 | 0.15561 | 2.4766 | 0.88042 | 0.058707 | 0.0034465
| 3 | 43 | 60.24 | 258.075 | 0.71381 | 0.4998 | 0.23342 | 1.6511 | 0.75248 | 0.038672 | 0.0014955
| 4 | 52 | 80.32 | 258.075 | 0.64741 | 0.6664 | 0.31123 | 1.2383 | 0.64519 | -0.0022252 | 4.9515e-06
| 5 | 58 | 100.4 | 258.075 | 0.57769 | 0.833 | 0.38903 | 0.99064 | 0.56035 | -0.017342 | 0.00030073
| 6 | 64 | 120.48 | 258.075 | 0.53121 | 0.9996 | 0.46684 | 0.82553 | 0.49327 | -0.037942 | 0.0014396
| 7 | 68 | 140.56 | 258.075 | 0.48378 | 1.1662 | 0.54465 | 0.7076 | 0.43949 | -0.04429 | 0.0019616
[10 empty] | Somme Erreur | 0.016845
Dimensions L x W x H
12.9" x 2.1" x 12.0" (328 mm x 53 mm x 305 mm)
Performance
2110 W (7201 BTU/Hr)
Fluid Compatibility
Water, Common Coolants
Wetted Path
Copper
Type
Tube-Fin Liquid-to-Air
Fluid Volume
29.5 in³ (483 ml)
Fin Material
Copper
Maximum Temperature
200°C (400°F)
Maximum Pressure
150 psi (10 BAR)
Maximum Flow Rate
4.0 gpm (15.1 lpm)
Liquid Pressure Drop
8.9 psi (0.6 BAR)
Air Pressure Drop
0.13 in H₂O (32.38 Pa)
Fan Plate
Included
Finish
Painted Black
Shipping Weight
15.5 lb (7.03 kg)

## 3000
https://www.boydcorpdirect.com/6220g1-copper-tube-fin-heat-exchanger/6220g1/
| Débit eau | 3.7 | lpm | Dimensions
| Cp eau | 4185 | J/kg/K | L | 588 | mm
| Cp air | 1004 | J/kg/K | W | 53 | mm
| Rho air | 1.2 | kg/m^3 | H | 305 | mm
|  |  |  | Masse | 8.21 | kg
| Power [W] | AsU | L [m] | W [m] | H [m] | Masse [kg] | Air DP [Pa] | Flow Air [m^3/min] | Water DP [bar] | Flow Water [lpm]
| 3000 | 195.7676 | 0.588 | 0.053 | 0.305 | 8.21 | 25 | 14 | 0.9 | 15.1
Efficacité | AirFlow | Q/dT | Cmin | Cmax | Efficacite | Vitesse air | Cr=Cmin/Cmax | NUT=AsU/Cmin | Efficacité calculée | Erreur | Erreur ^2
| m^3/min | W/°C | W/K | W/K | - | m/s
| 0 | 0 | 0 | 258.075 | 1 | 0 | 0 |  | 1
| 2 | 37.5 | 40.16 | 258.075 | 0.93376 | 0.18587 | 0.15561 | 4.8747 | 0.97705 | 0.043288 | 0.0018739
| 4 | 62.5 | 80.32 | 258.075 | 0.77814 | 0.37173 | 0.31123 | 2.4373 | 0.83692 | 0.058787 | 0.0034559
| 6 | 82 | 120.48 | 258.075 | 0.68061 | 0.5576 | 0.46684 | 1.6249 | 0.69212 | 0.011514 | 0.00013257
| 8 | 95 | 160.64 | 258.075 | 0.59138 | 0.74347 | 0.62245 | 1.2187 | 0.57951 | -0.011877 | 0.00014107
| 10 | 105 | 200.8 | 258.075 | 0.52291 | 0.92933 | 0.77807 | 0.97494 | 0.49442 | -0.028491 | 0.00081172
| 12 | 113 | 240.96 | 258.075 | 0.46896 | 1.1152 | 0.93368 | 0.81245 | 0.42919 | -0.039772 | 0.0015818
[10 empty] | Somme erreur | 0.007997
Dimensions L x W x H
22.9" x 2.1" x 12.0" (583 mm x 53 mm x 305 mm)
Performance
3000 W (10239 BTU/Hr)
Fluid Compatibility
Water, Common Coolants
Wetted Path
Copper
Type
Tube-Fin Liquid-to-Air
Fluid Volume
51.5 in³ (844 ml)
Fin Material
Copper
Maximum Temperature
200°C (400°F)
Maximum Pressure
150 psi (10 BAR)
Maximum Flow Rate
4.0 gpm (15.1 lpm)
Liquid Pressure Drop
12.9 psi (0.9 BAR)
Air Pressure Drop
0.10 in H₂O (24.91 Pa)
Fan Plate
Included
Finish
Painted Black
Shipping Weight
18.1 lb (8.21 kg)

## 7600
https://www.boydcorpdirect.com/6340-copper-tube-fin-heat-exchanger/6340/?F_All=Y
| Débit eau | 7.5 | lpm | Dimensions
| Cp eau | 4185 | J/kg/K | L | 699 | mm
| Cp air | 1004 | J/kg/K | W | 89 | mm
| Rho air | 1.2 | kg/m^3 | H | 564 | mm
|  |  |  | Masse | 16.42 | kg
| Power [W] | AsU | L [m] | W [m] | H [m] | Masse [kg] | Air DP [Pa] | Flow Air [m^3/min] | Water DP [bar] | Flow Water [lpm]
| 7600 | 500.07 | 0.699 | 0.089 | 0.564 | 16.42 | 18.75 | 14.15 | 0.2 | 37.8
Efficacité | AirFlow | Q/dT | Cmin | Cmax | Efficacite | Vitesse air | Cr=Cmin/Cmax | NTU=AsU/Cmin | Efficacité calculée | Erreur | Erreur ^2
| m^3/min | W/°C | W/K | W/K | - | m/s
| 0 | 0 | 0 | 523.125 | 1 | 0 | 0 |  | 1
| 5 | 100 | 100.4 | 523.125 | 0.99602 | 0.21138 | 0.19192 | 4.9808 | 0.97342 | -0.022596 | 0.00051057
| 10 | 155 | 200.8 | 523.125 | 0.77191 | 0.42276 | 0.38385 | 2.4904 | 0.8223 | 0.050385 | 0.0025387
| 15 | 195 | 301.2 | 523.125 | 0.64741 | 0.63414 | 0.57577 | 1.6603 | 0.67241 | 0.024995 | 0.00062476
| 20 | 225 | 401.6 | 523.125 | 0.56026 | 0.84552 | 0.76769 | 1.2452 | 0.55835 | -0.0019085 | 3.6423e-06
| 25 | 245 | 502 | 523.125 | 0.48805 | 1.0569 | 0.95962 | 0.99616 | 0.47336 | -0.014693 | 0.00021587
| 30 | 260 | 602.4 | 523.125 | 0.43161 | 1.2683 | 1.1515 | 0.83013 | 0.40883 | -0.022782 | 0.000519
| 35 | 280 | 702.8 | 523.125 | 0.39841 | 1.4797 | 1.3435 | 0.71154 | 0.35863 | -0.03978 | 0.0015824
[10 empty] | Somme Erreur | 0.0059949
Dimensions L x W x H
27.5" x 3.5" x 22.2" (699 mm x 89 mm x 564 mm)
Performance
7600 W (25939 BTU/Hr)
Fluid Compatibility
Water, Common Coolants
Wetted Path
Copper
Type
Tube-Fin Liquid-to-Air
Fluid Volume
106 in³ (1737 ml)
Fin Material
Aluminum
Maximum Temperature
200°C (400°F)
Maximum Pressure
150 psi (10 BAR)
Maximum Flow Rate
10.0 gpm (37.8 lpm)
Liquid Pressure Drop
3.0 psi (0.2 BAR)
Air Pressure Drop
0.11 in H₂O (27.40 Pa)
Fan Plate
Included
Finish
Painted Black
Shipping Weight
36.2 lb (16.42 kg)
Fitting
0.875” O.D. union fitting